THE PERFORMANCE OF CONSTRUCTED WETLANDS TREATING PRIMARY, SECONDARY AND DAIRY SOILED WATER IN IRELAND (A REVIEW)

# M.G. Healy* and C.J. O’ Flynn

Civil Engineering, National University of Ireland, Galway, Co. Galway, Rep. of Ireland.

* Corresponding author. Email: mark.healy@nuigalway.ie. Tel: +353 91 495364; Fax: +353 91 494507.

Published as: Healy, M.G., O’ Flynn, C.J. 2011. The performance of constructed wetlands treating primary, secondary and dairy soiled water in Ireland (a review). Journal of Environmental Management 92: 2348-2354.

ABSTRACT

In Ireland, no database detailing the design, influent loading rates or performance of constructed wetlands (CWs) exists.   On account of this, they are designed without any protocol based on empirical data.  The aim of this paper was to provide the first published data on the performance of free-water surface flow (FWSF) CWs treating primary and secondary-treated municipal wastewater, and agricultural dairy soiled water (DSW) in Ireland.  In total, the performance of thirty-four FWSF CWs, comprising fourteen CWs treating primary-treated municipal wastewater, thirteen CWs treating secondary-treated municipal wastewater, and seven CWs treating DSW, were examined.  In most CWs, good organic, suspended solids (SS) and nutrient removal was measured.  At an average organic loading rate (OLR) of 10 and 9 g biochemical oxygen demand (BOD) m-2 d-1, CWs treating primary and secondary wastewater removed 95 and 84% of influent BOD.  Constructed wetlands treating DSW had an average BOD removal of 98%.  At average SS loading rates of 6 and 14 g m-2 d-1, CWs treating primary and secondary wastewater had a 96 and an 82% reduction, and produced a final effluent with a concentration of 14 and 13 mg L-1.  Constructed wetlands treating DSW produced a final effluent of 34 mg L-1 (94% reduction).  Similar to other studies, all CWs examined had variable performance in ammonium-N (NH4+-N) removal, with average removals varying between 37% (for CWs treating secondary wastewater) and 88% (for CWs treating DSW).  Variable ortho-phosphorus (PO43--P) removal was attributable to different durations of operation, media types and loading rates.

Keywords: Municipal wastewater; dairy soiled water; free-water surface wetlands.

1. Introduction

The use of constructed wetlands (CWs) for the treatment of domestic, municipal (Healy and Cawley, 2002) and agricultural wastewaters (Harrington and McInnes, 2009) is gaining in popularity in Ireland.  This is mainly due to population distribution, as well as the unsuitability of some of the land for traditional septic tank and percolation areas.  In 2006, the area of land classified as rural was 67,628 km2 (with a population of 2,430,499 people), whereas the area of land classified as urban was 1338 km2 (with a population of 1,804,426 people) (CSO, 2006).  In 2006, 956,239 housing units (65.4%) were connected to a public sewage system, whilst 418,033 (28.6%) used individual septic tanks, with the latter mainly located in rural areas.  This equated to approximately 1.17 million people using septic tank and percolation systems as a means of treating their wastewater.  As most of the land in Ireland is unsuitable for percolation, municipal wastewater is conventionally treated using activated sludge treatment plants, which often use CWs as a polishing step.  Presently, there are over 140 CWs used for the treatment of municipal, industrial and agricultural wastewater in Ireland (Babatunde et al., 2008).  So-called ‘Integrated Constructed Wetlands’ have also become popular in Ireland (Harrington and McInnes, 2009).  This is essentially a traditional CW, but is designed with an ecosystem approach that promotes nature conservation and an integrated management of land, water and living resources (Harrington and McInnes, 2009).

European legislation including the Water Framework Directive (WFD) (EC, 2000) has focused attention on the effective treatment of domestic wastewater.  Present agricultural practice is governed by The European Communities (Good Agricultural Practice for Protection of Waters) Regulations 2010 (S.I. No. 610 of 2010), which places a responsibility on the individual farmer and the public authority to adhere to the conditions set out within the Nitrates Directive and the WFD to ensure good wastewater management practices.

In the period from 2004 to 2006, municipal activities (including sewage, water treatment plant effluent, septic tank effluent and diffuse urban inputs) were responsible for 33% of slightly polluted rivers, 43% of moderately polluted rivers and 54% of seriously polluted rivers (Clabby et al., 2008).  Agricultural activities (including diffuse and point sources of wastes) were responsible for approximately 37% of slightly polluted rivers, 24% of moderately polluted rivers, and 23% of seriously polluted rivers (Clabby et al., 2008).

Over the years, limited work has been conducted in Ireland on the treatment efficiency of CWs in terms of performance or nutrient uptake by the emergent vegetation (Healy et al., 2007a).  These studies focused on individual systems that were monitored over a number of years (Healy and Cawley, 2002; Dunne et al., 2005; Harrington et al., 2007).  Harty and Otte (2003) provided a database of CWs in Ireland, focused on their distribution and ecology, but had limited discussion on their treatment efficiency.  Babatunde et al. (2008) conducted the first survey of the performance of CWs in Ireland and provided the results from thirteen CWs with a range of influent biochemical oxygen demand (BOD) concentrations ranging from 7058±17,081 to 6.4±1.2 mg L-1, but did not distinguish between wastewater types.  Overall, Babatunde et al. (2008) reported the following removals: BOD: 76.8-99.8%; chemical oxygen demand (COD): 76.3-99.7%; and ammonium-nitrogen (NH4+-N): 67-99.9%.

The aim of this paper was to provide the first published data on the performance of free-water surface flow (FWSF) CWs treating primary-treated municipal wastewater (wastewater that has undergone settlement), secondary-treated municipal wastewater (wastewater that has undergone some type of biological treatment), and agricultural dairy soiled water (DSW) in Ireland.  Optimal design for CWs was well covered in the literature (Kadlec and Wallace, 2009) and, therefore, was not discussed.  The performance of subsurface horizontal flow (SSHF) CWs was not included in this paper, as no substantial water quality data sets were available from local authorities or other stakeholders.  Dairy soiled water is produced on dairy farms through the washing-down of milking parlors and holding areas.  It contains nutrients and other constituents that pose a potential threat to water quality if not managed correctly.  Typically, DSW is similar in composition to cattle slurry, but is more dilute.  In Ireland, it is defined as having a BOD concentration of less than 2,500 mg L-1 and a suspended solids (SS) concentration of less than 1% SS (S.I. No. 610 of 2010).  The CWs treating primary wastewater had population equivalents (PEs) between 30 and 1808 and the CWs treating secondary wastewater had PEs between 50 and 2240.

1.1 Wastewater characteristics of municipal wastewater and DSW in Ireland

Domestic wastewater flow typically follows a diurnal pattern, with small flows at night and large flows in the morning and evening.  A list of the average concentrations of primary wastewater in this study and other studies is tabulated in Table 1.

Volumes of water on farms used for wash-down of yard areas, milk spillage, yard area rainfall, and stormwater run-off lead to a final effluent of variable concentration and volume.  The water volumes generated may vary according to the practices applied by the farmers.  Factors such as frequency of milking and the number of cows present at the same time affect the volumes generated. Dairy soiled water production has been estimated at 50 L cow-1 d-1, but this value can frequently be exceeded especially where there is indifferent management of water usage.

Concentrations of organic matter and SS in dairy wastewater are significantly higher than municipal effluent, and tend to vary throughout the year (Rodgers et al., 2005).  Minogue et al. (2010) tested DSW quality from 60 Irish farms and the results obtained are presented in Table 1.  A comparison between the average DSW concentrations of Minogue’s study, the present study and studies in other locations in addition to Ireland is also presented in Table 1.

2. Methods

The data obtained for this study came from local authorities, landowners, and published literature (Healy and Cawley, 2002; Dunne et al., 2005; Harrington et al., 2007; Kayranli et al., 2010).  The study aimed to be as extensive as possible, and all available FWSF CWs with extensive water quality data sets were utilized.  Water quality parameters, such as total nitrogen (TN), total phosphorus (TP), or microbial quality parameters were not commonly measured by local authorities in Ireland, and were not included in the performance data.  In total, data from thirty-four CWs are presented.  This comprises fourteen CWs treating primary wastewater, thirteen CWs treating secondary wastewater, and seven CWs treating DSW.  The influent flow volumes to municipal CWs were known and are presented.  The agricultural CWs surveyed however were not instrumented with flow-measuring devices and only effluent concentrations were available.  While some results originated from published literature on identified experimental CWs, the data reported in this paper were not ascribed to specific CWs, as some information may be sensitive vis-à-vis poorly performing CWs.  In this review, the performance of the CWs were based on inlet and outlet concentrations. The removal efficiency was defined as:

(1)

where       was the average inlet concentration (mg L-1) and         was the outlet concentration (mg L-1).  It is important to note that the removal efficiency, as calculated in this paper, excludes the effects of dilution or evapotranspiration, which means that the results in this paper possibly attribute a greater treatment performance to CWs than would be the case if a mass removal, determined using a water balance, was calculated for each individual wetland.

3. Results and discussion

3.1 Organics

In this study, the average removals of BOD from CWs treating primary and secondary wastewater, and DSW were 95, 84, and 98%, respectively.  The removals recorded in this study were within the EPA guidelines of allowable minimum percentage reductions of 70 and 90% required for wastewater treatment plants treating primary wastewater (EEC, 1991).  Their respective average effluent concentrations of 12±7, 8±7 and 16±5 mg L-1 were also below the maximum allowable concentration (MAC) of 25 mg L-1.  Figures 1 and 2 illustrate the variability of influent and effluent concentrations.

Figure 1 and Figure 2 here

The average organic loading rates (OLRs) for CWs treating primary wastewater was 10 and 9 g m-2 d-1 for CWs treating secondary wastewater (Figure 3).  Organic loading rates not exceeding 6 g BOD m-2 d-1 are recommended for FWSF CWs (Healy et al., 2007b), but BOD removals of about 70% have been measured for OLRs of up to 28 g BOD m-2 d-1 (Healy et al., 2007b).  Of the CWs treating secondary wastewater, the removal of 84% was similar to other studies (online supplementary data).

Figure 3 here

Of the seven CWs treating DSW detailed in the present study, only one was fully instrumented to enable OLRs to be determined (Dunne et al., 2005).  In that study, farmyard DSW, collected in a three-chambered tank, was pumped to a CW comprising three FWSF CWs with a total area of 4265 m2 and a final monitoring pond with an area of 490 m2.  At an average OLR of 3.6 g BOD m-2 d-1, an average influent BOD concentration of 2806 mg L-1 was reduced to an average effluent concentration of 20 mg L-1 (Dunne et al., 2005).  At a similar loading rate (4.4 g BOD m-2 d-1), Smith et al. (2006) measured BOD removals of up to 99% in a FWSF CW planted with cattails (Typha latifolia L.) and fresh water grasses.  In a study of a FWSF CW treating milkroom parlor wastewater in Connecticut, USA, Newman et al. (2000) found that, under an OLR of approximately 18 g BOD m-2 d-1, 77% of BOD was removed and no nitrification occurred (online supplementary data).

Although the data sets were too small to detect any discernable trend, the following observations may be made: (i) CWs treating primary wastewater produced consistently good BOD removals – even at OLRs of up to 40 g BOD m-2 d-1 (ii) the ratio of the effluent BOD concentration (Ce) to the influent concentration (Co) was less than 0.21 (iii) CWs treating secondary wastewater, even at relatively low OLRs of less than 5 g BOD m-2 d-1, did not perform as well.  This may however, have been a function of the low influent concentration (50 mg BOD L-1) and the associated difficulties in adequate resolution of data.  One CW treating secondary wastewater was malfunctioning, and had a Ce/Co of approximately 2.5.  It also produced similar poor values – in terms of Ce/Co - for COD and SS.

The average removals of COD from primary and secondary wastewater was 88 and 72%, respectively, and the average final effluent concentrations were 53±18 and 45±27 mg L-1 – well below the MAC of 125 mg L-1.  Average removals of COD from the CWs treating secondary wastewater was 72%, and from CWs treating DSW were 91%.  However, average effluent concentrations were 162 mg L-1, which was much higher than the MAC.  The average OLR for primary and secondary wastewater was 22 and 24 g COD m-2 d-1.  Good removals – in terms of Ce/Co – were observed, even at OLRs of up to 90 and 45 g COD m-2 d-1 for primary and secondary wastewater, respectively.  Similar results in terms of COD and BOD removal were obtained in other countries (online supplementary data).

3.2 Suspended Solids

Suspended solids removals from CWs treating primary and secondary wastewater, and DSW were 96, 82 and 94%, respectively, and produced respective final average effluent concentrations of 14±7, 13±7 and 34±31 mg L-1.  The CWs treating primary and secondary wastewater produced final effluent concentrations below the MAC of 35 mg L-1, but the CWs treating DSW frequently exceeded the MAC (Figure 2).  In addition, if short circuiting occurs, average water retention time within the wetland will be limited, giving rise to poor SS removals (USEPA, 1999).

The average SS loading rates for CWs treating primary domestic and secondary wastewater were 6 and 14 g m-2 d-1, respectively.  Suspended solids loading rates of under 5 g SS m-2 d-1 for FWSF CWs are recommended (Healy et al., 2007b).  Dunne et al. (2005) found SS removals of almost 100% at SS loading rates of approximately 1 g SS m-2 d-1.  At a similar loading rate (2.1 g SS m-2 d-1), Smith et al. (2006) measured SS removals of greater than 95%, whereas at a loading rate of 9 g SS m-2 d-1, Newman et al. (2000) measured reductions of 90%.

Potentially confounding factors such as temperature and hydraulic loading rate (HLR) may also affect SS removal.  Smith et al. (2006) investigated the effect of temperature (>10oC and <10oC) on the SS removal performance of a FWSF CW and found no difference.  However, with similar SS concentrations but with elevated SS loading rates (9 g SS m-2 d-1), Newman et al. (2000) found seasonal differences (92% in summer and 78% in winter).  Hydraulic loading rate and hydraulic retention time (HRT) are also linked to performance.  Knowlton et al. (2002) and Smith et al. (2006) found that large losses of SS occurred in the months following increased loading.  As the HLR is related to the HRT, a reduced HRT does not provide adequate time for settling of SS (Kadlec and Wallace, 2009).

3.3 Nitrogen

Total nitrogen is composed of NH4+-N, nitrite (NO2--N), nitrate (NO3--N) and organic matter.  The data sets collected from local authorities mainly tabulated NH4+-N, therefore this parameter is the only one reported in this paper.  Average final NH4+-N effluent concentrations for CWs treating primary and secondary wastewater, and DSW were 11±13, 6±7 and 6±5 mg L-1, respectively.  They represented removal efficiencies of 77, 37 and 88% for the primary, secondary and DSW, respectively.  Excluding the dilution effect of rainfall, the mass removals may have been much lower. Factors such as low water temperature and short HRT may affect N removals within CWs (Reinhardt et al., 2006) and may have contributed to some low removals measured in these CWs.

Constructed wetlands are capable of good organic, SS and fecal coliform removals, but commonly have poor NH4+-N removals (Toet et al., 2005a).  Even under significantly reduced OLRs, FWSF CWs have under-performed.  In the present study, in CWs with OLRs of 10 g BOD m-2 d-1 treating primary wastewater and 9 g BOD m-2 d-1 in CWs treating secondary wastewater, the NH4+-N removals were highly variable (Figure 3).  This may be due to re-mineralisation of organic matter, lack of oxygenated sites within the wetland and decay of vegetation.  The choice of vegetation may be significant in TN removal.  The study detailed in this paper was carried out on FWSF CWs planted with a mixture of emergent, submersed and floating vegetation.  Toet et al. (2005a) found that in a FWSF CW planted with a mixture of emergent and submersed vegetation and treating final effluent from a sewage treatment plant, TN removal was 26% (expressed in g N m-2 yr-1) and was mainly reduced in wetland cells planted with emergent vegetation.  In addition, the decay of vegetation during cold months may release organic N back into the system, which is then available for ammonification (Kadlec and Wallace, 2009).  Therefore, a CW may become a source of NH4+-N.

3.4 Phosphorus

Similar to TN, TP was not frequently measured by local authorities.  The phosphorus (P) parameter tested was frequently ortho-P (PO43--P).  The ability of CWs to retain P was dependent on the P loading rate, the media type, vegetation, and duration of operation (Healy et al., 2007b), although changes in pH and redox potential could also release P from the system.  65 to 95% of P may be removed at loading rates of less than 5 g TP m-2 yr-1 (Healy et al., 2007b).  Phosphorus is removed through short-term or long-term storage, with most removal often occurring near the inlet initially, before extending throughout the wetland over time as those sites become P-saturated (Jamieson et al., 2002).  Uptake by bacteria, algae and duckweed (Lemma spp.), and macrophytes provides an initial removal mechanism.  However, this is only a short-term P storage as 35%-75% of P stored is eventually released back into the water upon dieback of algae and microbes, as well as plant residues.  The only long-term P storage in the wetland is via peat accumulation and substrate fixation.  The efficiency of long-term peat storage is a function of the loading rate and also depends on the amount of native iron, calcium, aluminum, and organic matter in the substrate.

The CWs surveyed in this study have different loading rates, lifespans and dilutions, so the removals quoted are not necessarily representative of performance.  Similar analysis problems were reported by Smith et al. (2006), who found that factors such as SS loading rate and water depth also affected performance.  The average final effluent PO43--P concentrations of CWs treating primary and secondary wastewater, and DSW were 3±2 (a 64% removal), 5±5 (a -54% removal) and 3±2 mg L-1 (an 80% removal), respectively.  These were all in excess of the wastewater treatment plant limit of 0.7 mg PO43--P L-1 required for discharge to rivers (S.I. No. 7 of 1992).  Lower removals and even negatives have been reported in other studies (Benham and Mote, 1999).  This is often related to a small HRT, where there is a reduced contact time for adsorption to occur.

3.5 Gaps in constructed wetland research in Ireland.

The aim of this paper was to collate all available information on the performance of CWs in Ireland.  However, no database detailing their design, influent loading rates or performance exists.  This means that many aspects central to their performance, such as, for example, choice of vegetation, optimal loading rates or the interaction between water temperature and removal rates, cannot be determined based on empirical data.  As such, a variety of design criteria are used in Ireland without any design protocol based on synthesized empirical data.  Some potential gaps in CW research in Ireland, which may be potentially addressed by a centralized database, are now identified.

3.5.1 Effect of vegetation on performance

In Ireland, a mixture of emergent, submersed and floating vegetation are used in CWs (Harty and Otte, 2003).  As the type of vegetation used to colonize CWs affects performance (Toet et al., 2005a; Bastviken et al., 2007, 2009), it is important that appropriate vegetation is identified.  This issue was investigated by Bastviken et al. (2009) in a series of FWSF CWs in Sweden.  Nitrate removal (kg ha-1 yr-1) was higher in CWs colonised by emergent vegetation – P. australis (Trin.), G. maxima (Hartm.) and Phalaris arundinacea (L.) - than those planted with submersed vegetation – E. Canadensis (Rich.), Myriophyllum alterniflorum (DC.) and Ceratophyllum demersum (L.).  Similar findings were made by Toet et al. (2005a), who found higher NO3 removals in FWSF CWs planted with P. australis and T. latifolia than those planted with submersed plants – mainly Elodea nuttallii, Ceratophyllum demersum and Potamogeton spp.- and algae.

In addition, the management of vegetation is important for the sustainability of a CW.  An appropriate water height and an optimal ratio of wetland vegetation to open water are crucial for sustaining treatment efficacy and habitat value (Thullen et al., 2002).  Harvesting, although perhaps not contributing significantly to nutrient removal (Healy et al., 2007a), may help improve the functioning of a CW as dense vegetation can contribute towards internal nutrient loading as plants decompose (Sartoris et al., 2000).

3.5.2 Effect of hydraulic loading rate, residence time and temperature on performance

The determination of a critical HLR, HRT and water temperature which provides optimal performance is crucial. Related to this is the relationship between OLR and outlet concentration.  Optimal OLRs for CWs are well defined (Healy et al., 2007b), but HLR and HRT can also impact on performance (Kadlec and Wallace, 2009).  There is a lack on consensus in the literature regarding the nature of their impact: Kadlec (2005) found that a high HLR resulted in high removals of NO3 due to increased availability of NO3 for denitrifying bacteria, whereas Spieles and Mitsch (2000) speculated that a high HLR oxygenated the sediment surface, re-suspended organic material and consequently produced low removals of NO3.  Similarly, there is a lack of agreement on the impact of HRT: Toet et al. (2005b) found that the mass removal of NO3 was affected by HRT, but Bastviken et al. (2009) and Lu et al. (2009) found no significant difference.  Reduction of SS and organics are also affected by HLR and HRT, with large losses occurring following increased loading onto a CW (Smith et al., 2006).

Water temperature also impacts on performance (Poach et al., 2004; Lu et al., 2009), but, in Ireland, CWs are still designed using rate constants based on empirical sizing equations developed from first order decay curves fitted to inflow/outflow from CWs in warmer climates.  This does not account for the interaction between biological, chemical and physical processes specific to Ireland.  Analytical models based on Irish data need to be developed.

4. Conclusions

The main conclusions are:

- At average OLRs of 10 and 9 g BOD m-2 d-1, CWs treating primary and secondary wastewater had average BOD removals of 95 and 84%, respectively.

- At loading rates of 6 and 14 g SS m-2 d-1, CWs treating primary and secondary wastewater produced final effluents with an average concentration of 14 and 13 mg L-1.  Constructed wetlands treating DSW produced an average final effluent marginally below the MAC.

- The performance of the CWs in the reduction of NH4+-N and PO43--P was highly variable.

- In most CWs in Ireland, only the final effluent is continuously monitored.  Individual databases, often with limited water quality parameters, are held mainly by local authorities.  No centralized database exists that allows the inquisition of performance data on the basis of, say, location, wetland age, wastewater type, or hydraulic loading rate.  A centralized database is needed that may be used to inform design protocols for CWs in Ireland.  A detailed database could, in time, be used to develop empirical equations that could be used to design CWs.  Related to this, more thorough monitoring of CWs needs to be employed: influent and effluent water quality, along with flow data (if possible) needs to be monitored.

5. Acknowledgements

The authors acknowledge the assistance of representatives from local authorities and landowners in Ireland in the completion of this study.

Appendix

Supplementary data associated with this article can be found in the online version at: (doi here)

6. References

Babatunde, A.O., Zhao, Y.Q., O’Neill, M., O’Sullivan, B., 2008.  Constructed wetlands for environmental pollution control: a review of developments, research and practice in Ireland.  Env. Int. 34, 116-126.

Bastviken, S.K., Eriksson, P.G., Ekström, A., Tonderski, K., 2007.  Seasonal denitrification potential in wetland sediments with organic matter from different plant species.  Wat. Air Soil Poll. 183, 25-35.

Bastviken, S.K., Weisner, S.E.B., Thiere, G., Svensson, J.M., Ehde, P.M., Tonderski, K.S., 2009.  Effects of vegetation and hydraulic load on seasonal nitrate removal in treatment wetlands.  Ecol. Eng. 35, 946-952.

Benham, B.L., Mote, C.R., 1999.  Investigating dairy lagoon treatability in a laboratory-scale constructed wetland system.  Trans. Am. Soc. Agr. Eng. 42, 495-502.

Clabby, K.J., Bradley, C., Craig, M., Daly, D., Lucey, J., O’Boyle, S., O’Donnell, C., McDermott, G., McGarrigle, M., Tierney, D., Wilkes, R., Bowman, J., 2008.  Water Quality in Ireland 2004–2006.  EPA, Wexford.  http://www.epa.ie/downloads/pubs/water/waterqua/waterrep/.  Accessed 19/1/11.

CSO, 2006.  Census of Population 2006 preliminary results.  Dublin. http://www.cso.ie/census/Census2006_Principal_Demographic_Results.htm.  Accessed 12/1/11.

Cumby, T.R., Brewer, A.J., Dimmock, S.J., 1999.  Dirty water from dairy farms, I: biochemical characteristics.  Biores. Tech. 67, 155-160.

Dunne, E.J., Culleton, N., O’Donovan, G., Harrington, R., Olsen, A.E., 2005.  An integrated constructed wetland to treat contaminants and nutrients from dairy farmyard dirty water.  Ecol. Eng. 24, 221-254.

EC, 2000. Water Framework Directive (2000/60/EC) establishing a framework for community action in the field of water policy.  Available at: http://www.wfdireland.ie/.  Accessed 19/1/11.

Eliasson, J., 2003.  Rule development committee issue research report draft – septic tank effluent values.  Washington State Department of Health Wastewater Management Program. http://www.doh.wa.gov/ehp/ts/ww/TechIssueReports/STE-Values-JME.pdf .  Accessed 20/1/11.

EEC, 1991.  Council Directive of 21 May 1991 concerning urban waste water treatment (91/271/EEC).  Official Journal of the European Union. OJ L 135.30.5. p. 45.  http://eur-lex.europa.eu/LexUriServ/LexUriServ.do?uri=CONSLEG:1991L0271:20081211:EN:PDF.  Accessed 17/1/11.

Environmental Protection Agency, 2009.  Code of practice.  Wastewater treatment and disposal systems serving single houses (p.e. < 10).  Environmental Protection Agency, Wexford, Ireland.  104 pp. http://www.epa.ie/downloads/advice/water/wastewater/name,27046,en.html.  Accessed 17/1/11.

Harrington, R., Carroll, P., Carty, A.H., Keohane, J., Ryder, C., 2007.  Integrated constructed wetlands : concept, design, site evaluation and performance.  Int. J. Wat. 3, 243-256.

Harrington, R., McInnes, R., 2009.  Integrated constructed wetlands (ICW) for livestock wastewater management.  Biores. Tech. 100, 5498-5505.

Harty, F., Otte, M.L., 2003.  Constructed wetlands for treatment of waste water, in: Otte, M.L. (Ed.), Wetlands of Ireland: distribution, ecology, uses and economic value.  University College Dublin Press, pp. 182-190.

Healy, M.G. Cawley, A.M., 2002.  Performance of a constructed wetland in western Ireland.  J. Env. Qual. 17, 1739-1747.

Healy, M.G., Newell, J., Rodgers, M., 2007a.  Harvesting effects on biomass and nutrient retention in Phragmites australis in a free-water surface constructed wetland in western Ireland.  Biol. and Env: Proceed. Royal Ir. Acad. 107B, 139-145.

Healy, M.G., Rodgers, M., Mulqueen, J., 2007b.  Treatment of dairy wastewater using constructed wetlands and intermittent sand filters.  Biores. Tech. 98, 2268-2281.

Jamieson, T.S., Stratton, G.W., Gordon, R., Madani, A., 2002.  Phosphorus adsorption characteristics of a constructed wetland soil receiving dairy farm wastewater.  Can. J. Soil Sci. 82, 97-104.

Kadlec, R.H., 2005.  Nitrogen farming for pollution control.  J. Environ. Sci. Health 40, 1307-1330.

Kadlec, R.H., Wallace, S., 2009.  Treatment Wetlands, second ed. CRC Press, Boca Raton, FL.

Kayranli, B., Scholz, M., Mustafa, A., Hofmann, O., Harrington, R., 2010.  Performance evaluation of integrated constructed wetlands treating domestic wastewater.  Water Air Soil Pollut. 210, 435-451.

Knight, R.L., Payne Jr., V.W.E., Borer, R.E., Clarke Jr., R.A., Pries, J.H., 2000.  Constructed wetlands for livestock management.  Ecol. Eng. 15, 41-55.

Knowlton, M.F., Cuvellier, C., Jones, J.R., 2002.  Initial performance of a high capacity surface-flow treatment wetland.  Wetlands 22, 522-527.

Lu, S., Zhang, P., Jin, X., Xiang, C., Gui, M., Zhang, J., Li, F., 2009.  Nitrogen removal from agricultural runoff by full-scale constructed wetland in China.  Hydrobiol. 621, 115-126.

Minogue, D. Coughlan, F., Murphy, P., French, P., Bolger, T., 2010.  Characterisation of soiled water on Ireland dairy farms. BSAS/WPSA/Agricultural Research Forum Conference.  Queen’s University, Belfast. 12-14 April, 2010.

Newman, J.M., Clausen, J.C., Neafsey, J.A., 2000.  Seasonal performance of a wetland constructed to process dairy milkhouse wastewater in Connecticut.  Ecol. Eng. 14, 181-198.

Poach, M.E., Hunt, P.G., Reddy, G.B., Stone, K.C., Johnson, M.H., Grubbs, A., 2004.  Swine treatment by marsh-pond-marsh constructed wetlands under varying nitrogen loads.  Ecol. Eng. 23, 165-175.

Reinhardt, M., Müller, B., Gächter, R., Wehrli, B., 2006.  Nitrogen removal in a small constructed wetland: an isotope mass balance approach.  Env. Sci. and Tech. 40, 3313-3319.

Rodgers, M., Healy, M.G., Mulqueen, J., 2005.  Organic carbon removal and nitrification of high strength wastewaters using stratified sand filters.  Wat. Res. 39, 3279-3286.

Sartoris, J.J., Thullen, J.S., Barber, L.B., Salas, D.E., 2000.  Investigation of nitrogen transformations in a southern California constructed wastewater treatment wetland.  Ecol. Eng. 14, 49-65.

Smith, E., Gordon, R., Madani, A., Stratton, G., 2006.  Year-round treatment of dairy wastewater by constructed wetlands in Atlantic Canada.  Wetlands 26, 349-357.

Spieles, D.J., Mitsch, W.J., 2000.  The effects of season and hydrologic and chemical loading on nitrate retention in constructed wetlands: a comparison of low- and high-nutrient riverine systems.  Ecol. Eng. 14, 77-91.

Thullen, J.S., Sartoris, J.J., Walton, W.E., 2002.  Effects of vegetation management in constructed wetland treatment cells on water quality and mosquito production.  Ecol. Eng. 18, 441-457.

Toet, S., Logtestijn, R.S.P.V., Schreijer, M., Kampf, R., Verhoeven, J.T.A., 2005a.  The functioning of a wetland system used for polishing effluent from a sewage treatment plant.  Ecol. Eng. 25, 101-124.

Toet, S., Logtestijn, R.S.P.V., Kampf, R., Schreijer, M., Verhoeven, J.T.A., 2005b.  The effect of hydraulic retention time on the removal of pollutants from sewage treatment plant effluent in a surface-flow wetland system.  Wetlands 25, 375-291.

U.S. Environmental Protection Agency, 1999.  Constructed wetlands treatment of municipal wastewaters. National Risk Management Research Laboratory, OH. 165pp. http://www.epa.gov/owow/wetlands/pdf/Design_Manual2000.pdf.   Accessed 20/1/11.

Figure Captions

Figure 1. Average influent and effluent concentrations (± standard deviation) from wetlands treating primary and secondary treated municipal wastewater (dark box = influent; white box = effluent)

Figure 2. Average influent and effluent concentrations (± standard deviation) from wetlands treating dairy soiled water (dark box = influent; white box = effluent)

Figure 3. Relationship between loading rates for BOD, COD, SS, NH4+-N and PO43--P (g m-2 d-1) and performance, expressed as final effluent concentration (Ce) divided by influent concentration (Co), in wetlands treating primary (top) and secondary wastewater (bottom). BOD – closed square; COD – closed diamond; SS – closed triangle; NH4+-N – open diamond; PO43-- P – open square.

Table 1.  Comparison of mean primary municipal wastewater and dairy soiled water (DSW) concentrations from Ireland and elsewhere.

___________________________________________________________________________________________________________________________________________

Wastewater 	Location	n1	 		Parameter																						Reference

type									BOD			SS			TN			NH4+-N		Org N		TP		PO43--P		Total solids

________________________________ mg L-1  ______________________________	%

Municipal

Primary2		Ireland					150-500			200-700					22-80					5-20							EPA, 2009

Ireland		14			218±215		334±698				50±30							8±5						In the present study

USA		9			153±101		41±24																			Eliasson, 2003

DSW			Ireland		60			2246±2112		5120±5865	587±536	212±206	381±413	80±68	37±53					Minogue et al., 2010

Ireland		7			998±1034		535±434				48±25							15±7					In the present study

UK			20			2260-9670								310-580							340-490		0.57-1.65	Cumby et al., 1999

USA		32-3743		442				361			103			351														Knight et al., 2000

___________________________________________________________________________________________________________________________________________1 n = number of study locations.

2 Primary = wastewater that has undergone settlement. Secondary wastewater performance results are excluded as various biological treatment methods will yield varying results.

3 n = 442 for BOD; n = 361 for SS; n = 351 for NH4-N; n = 32 for TN.

Figure 1. Average influent and effluent concentrations (± standard deviation) from wetlands treating primary- and secondary-treated municipal wastewater (dark box = influent; white box = effluent)

|  | Primary wastewater | Secondary wastewater |
| --- | --- | --- |
| BOD (mg L-1) |  |  |
| COD (mg L-1) |  |  |
| SS (mg L-1) |  |  |
| NH4+-N (mg L-1) |  |  |
| PO43--P (mg L-1) |  |  |

Figure 2. Average influent and effluent concentrations (± standard deviation) from wetlands treating dairy soiled water (dark box = influent; white box = effluent)

| BOD (mg L-1) |  |
| --- | --- |
| COD (mg L-1) |  |
| SS (mg L-1) |  |
| NH4+-N (mg L-1) |  |
| PO43--P (mg L-1) |  |

Figure 3. Relationship between loading rates for BOD, COD, SS, NH4+-N and PO43--P (g m-2 d-1) and performance, expressed as final effluent concentration (Ce) divided by influent concentration (Co), in wetlands treating primary (top) and secondary wastewater (bottom). BOD – closed square; COD – closed diamond; SS – closed triangle; NH4+-N – open diamond; PO43-- P – open square.